## Exercises
© 2022 I&E Systems Pty Ltd
Experiment with the calculations to explore the effect of changing input values and architectures.
1. For each architecture, Prepare an XY plot of RRFAVG and MTTFS to compare different architectures,
1oo1, 1oo2, 1oo3, 2oo2, 2oo3, 2oo4, 3oo3, 3oo4,assuming these parameter sets:
MTBFDU = 300 y, MTBFDD = 100 y, MTBFS = 300 y, MTTR = 3 days, β =0.1
and
MTBFDU = 30 y, MTBFDD = 1,000 y, MTBFS = 1,000 y, MTTR = 3 days, β =0.1
2. Produce a stacked column chart using that same parameter set for each architecture out of:
1oo1, 1oo2, 1oo3, 2oo2, 2oo3, 2oo4, 3oo3 and 3oo4
to show the relative contribution of each term in the equation to the overall PFDAVG.
Compare results for β = 0, 0.01, 0.02, 0.05 and 0.1.
3. Repeat the exercise but leaving β =0.1 and varying βD = 0, 0.01, 0.02, 0.05 and 0.1.
4. For each architecture 1oo1, 1oo2, 2oo3, 2oo2, plot the variation of RRFAVG against these values of T1:
T1 = 0.3 y, T1 = 1 y, T1 = 3 y, T1 = 10 y
with
MTBFDU = 100 y, MTBFDD = 300 y, MTBFS = 300 y, MTTR = 3 days, β =0.1
5. For each architecture, plot the variation of RRFAVG against these values of MTBFDU:
MTBFDU = 30 y, MTBFDU = 100 y, MTBFDU = 300 y, MTBFDU = 1,000 y
with
T1 = 1 y, MTBFDD = 300 y, MTBFS = 300 y, MTTR = 3 days, β =0.1
6. For each architecture, plot the variation of RRFAVG against these values of MTBFDD:
MTBFDD = 30 y, MTBFDD = 100 y, MTBFDD = 300 y, MTBFDD = 1,000 y
with
T1 = 1 y, MTBFDU = 100 y, MTBFS = 300 y, MTTR = 3 days, β =0.1
7. For each architecture, plot the variation of RRFAVG against these values of MTTR:
MTTR = 1 day, MTTR = 3 days, MTTR = 10 days, MTTR = 30 days, MTTR = 100 days
with
T1 = 1 y, MTBFDU = 300 y, MTBFS = 300 y, MTBFDD = 300 y, β =0.1
and with
T1 = 1 y, MTBFDU = 1,000 y, MTBFS = 300 y, MTBFDD = 300 y, β =0.1
8. For each architecture, plot the variation of RRFAVG against these values of MTBFDN:
MTBFDN = 300 y, MTBFDN = 1,000 y, MTBFDN = 3,000 y, MTBFDN = 10,000 y
with
T1 = 1 y, T2 = 10 y, MTBFDU = 100 y, MTBFS = 300 y, MTTR = 3 days, MTBFDD = 300 y, β = 0.1
9. For each architecture, plot the variation of RRFAVG against these values of T2:
T2 = 1 y, T2 = 3 y, T2 = 10 y, T2 = 30 y
with
T1 = 1 y, MTBFDU = 100 y, MTBFDN = 1,000 y, MTBFS = 300 y, MTTR = 3 days, MTBFDD = 300 y, β = 0.1
10. For each architecture, plot the variation of RRFAVG against these values of β:
,β = 0, β = 0.01, β = 0.02, β = 0.05, β = 0.1
with
T1 = 1 y, T2 = 10 y, MTBFDU = 100 y, MTBFDN = 10,000 y, MTBFS = 300 y, MTTR = 3 days,
MTBFDD = 300 y

## Architectures
© 2022 I&E Systems Pty Ltd
Round to | 2 | significant figures | [6 empty] | Shading indicates the cells for data entry | [22 empty] | The colour shading highlights the largest term
[24 empty] | β for 1oo2 architecture |  | β for MooN architecture
PFDAVG | RRFAVG | MTTFS (years) |  |  | M | N | Voting | MTBFDU (years) | λDU (pa) | MTBFDD | λDD | DC | MTBFDN | λDN | PTC | MTBFS | λS | T1 (years) | T2 (years) | MTTR (days) | MTTR (years) | MRT (days) | MRT (years) | β | βD | MooN β | MooN βD | PFDAVG | RRFAVG | MTTFS (years) |  | Voted T1 term | CCF T1 term | Voted T2 term | CCF T2 term | Voted λDD term | CCF λDD term | PFDAVG |  | STR β | Voted STR term | CCF STR term | STR
0.01 | 95 | 150 |  |  | 1 | 1 | 1oo1 | 50 | 0.02 | 300 | 0.0033333 | 14.29% | 10000 | 0.0001 | 99.5% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0 | 0 | 0.010477 | 95.4436 | 150 | 1 | 0.00995 | 0 | 0.0005 | 0 | 2.7397e-05 | 0 | 0.010477 | 1 | 0 | 0.0066667 | 0 | 0.0066667
0.0012 | 870 | 75 |  |  | 1 | 2 | 1oo2 | 50 | 0.02 | 300 | 0.0033333 | 14.29% | 10000 | 0.0001 | 99.5% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.1 | 0.1 | 0.0011549 | 865.8511 | 75 | 1 | 0.00010692 | 0.000995 | 2.7e-07 | 5e-05 | 6.0799e-10 | 2.7397e-06 | 0.0011549 | 2 | 0 | 0.013333 | 0 | 0.013333
0.00053 | 1900 | 50 |  |  | 1 | 3 | 1oo3 | 50 | 0.02 | 300 | 0.0033333 | 14.29% | 10000 | 0.0001 | 99.5% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.05 | 0.05 | 0.00052556 | 1902.7351 | 50 | 1 | 1.6892e-06 | 0.0004975 | 2.1434e-10 | 2.5e-05 | 1.7632e-14 | 1.3699e-06 | 0.00052556 | 3 | 0 | 0.02 | 0 | 0.02
0.021 | 48 | 1500 |  |  | 2 | 2 | 2oo2 | 50 | 0.02 | 300 | 0.0033333 | 14.29% | 10000 | 0.0001 | 99.5% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0 | 0 | 0.020955 | 47.7218 | 1498.358 | 2 | 0.0199 | 0 | 0.001 | 0 | 5.4795e-05 | 0 | 0.020955 | 2 | 1 | 7.3059e-07 | 0.00066667 | 0.0006674
0.0019 | 540 | 1000 |  |  | 2 | 3 | 2oo3 | 50 | 0.02 | 300 | 0.0033333 | 14.29% | 10000 | 0.0001 | 99.5% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.15 | 0.15 | 0.0018585 | 538.0825 | 997.813 | 3 | 0.00028612 | 0.0014925 | 7.225e-07 | 7.5e-05 | 1.6269e-09 | 4.1096e-06 | 0.0018585 | 6 | 1.5 | 2.1918e-06 | 0.001 | 0.0010022
0.00064 | 1600 | 850 |  |  | 2 | 4 | 2oo4 | 50 | 0.02 | 300 | 0.0033333 | 14.29% | 10000 | 0.0001 | 99.5% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.06 | 0.06 | 0.00063519 | 1574.3317 | 853.9343 | 4 | 6.5455e-06 | 0.000597 | 8.3058e-10 | 3e-05 | 6.8323e-14 | 1.6438e-06 | 0.00063519 | 12 | 1.75 | 4.3836e-06 | 0.0011667 | 0.0011711
0.031 | 32 | 3000 |  |  | 3 | 3 | 3oo3 | 50 | 0.02 | 300 | 0.0033333 | 14.29% | 10000 | 0.0001 | 99.5% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0 | 0 | 0.031432 | 31.8145 | 2999.9989 | 3 | 0.02985 | 0 | 0.0015 | 0 | 8.2192e-05 | 0 | 0.031432 | 6 | 0.5 | 1.201e-10 | 0.00033333 | 0.00033333
0.0024 | 420 | 2500 |  |  | 3 | 4 | 3oo4 | 50 | 0.02 | 300 | 0.0033333 | 14.29% | 10000 | 0.0001 | 99.5% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.175 | 0.175 | 0.002374 | 421.234 | 2499.997 | 6 | 0.00053907 | 0.0017412 | 1.3613e-06 | 8.75e-05 | 3.0653e-09 | 4.7945e-06 | 0.002374 | 24 | 0.6 | 4.8039e-10 | 0.0004 | 0.0004
|  |  | Factor of change in RRF and MTTFs between the upper and lower sets of parameters | [22 empty] | #N/A | #N/A |  |  |  | #VALUE! | #VALUE! | #N/A | #VALUE! | #N/A | #VALUE! | #N/A |  | 1 | 0 | #NUM! | 0
0.0055 | 180 | 150 | 1.9128 | 1 | 1 | 1 | 1oo1 | 100 | 0.01 | 300 | 0.0033333 | 25% | 10000 | 0.0001 | 99% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0 | 0 | 0.0054774 | 182.5685 | 150 | 1 | 0.00495 | 0 | 0.0005 | 0 | 2.7397e-05 | 0 | 0.0054774 | 1 | 0 | 0.0066667 | 0 | 0.0066667
0.00057 | 1700 | 75 | 2.0104 | 1 | 1 | 2 | 1oo2 | 100 | 0.01 | 300 | 0.0033333 | 25% | 10000 | 0.0001 | 99% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.1 | 0.1 | 0.00057447 | 1740.7257 | 75 | 1 | 2.6463e-05 | 0.000495 | 2.7e-07 | 5e-05 | 6.0799e-10 | 2.7397e-06 | 0.00057447 | 2 | 0 | 0.013333 | 0 | 0.013333
0.00027 | 3600 | 50 | 1.9176 | 1 | 1 | 3 | 1oo3 | 100 | 0.01 | 300 | 0.0033333 | 25% | 10000 | 0.0001 | 99% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.05 | 0.05 | 0.00027408 | 3648.5957 | 50 | 1 | 2.0798e-07 | 0.0002475 | 2.1434e-10 | 2.5e-05 | 1.7632e-14 | 1.3699e-06 | 0.00027408 | 3 | 0 | 0.02 | 0 | 0.02
0.011 | 91 | 1500 | 1.9128 | 1 | 2 | 2 | 2oo2 | 100 | 0.01 | 300 | 0.0033333 | 25% | 10000 | 0.0001 | 99% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0 | 0 | 0.010955 | 91.2842 | 1498.358 | 2 | 0.0099 | 0 | 0.001 | 0 | 5.4795e-05 | 0 | 0.010955 | 2 | 1 | 7.3059e-07 | 0.00066667 | 0.0006674
0.00089 | 1100 | 1000 | 2.0808 | 1 | 2 | 3 | 2oo3 | 100 | 0.01 | 300 | 0.0033333 | 25% | 10000 | 0.0001 | 99% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.15 | 0.15 | 0.00089315 | 1119.6378 | 997.813 | 3 | 7.0812e-05 | 0.0007425 | 7.225e-07 | 7.5e-05 | 1.6269e-09 | 4.1096e-06 | 0.00089315 | 6 | 1.5 | 2.1918e-06 | 0.001 | 0.0010022
0.00033 | 3000 | 850 | 1.928 | 1 | 2 | 4 | 2oo4 | 100 | 0.01 | 300 | 0.0033333 | 25% | 10000 | 0.0001 | 99% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.06 | 0.06 | 0.00032945 | 3035.3566 | 853.9343 | 4 | 8.0591e-07 | 0.000297 | 8.3058e-10 | 3e-05 | 6.8323e-14 | 1.6438e-06 | 0.00032945 | 12 | 1.75 | 4.3836e-06 | 0.0011667 | 0.0011711
0.016 | 61 | 3000 | 1.9128 | 1 | 3 | 3 | 3oo3 | 100 | 0.01 | 300 | 0.0033333 | 25% | 10000 | 0.0001 | 99% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0 | 0 | 0.016432 | 60.8562 | 2999.9989 | 3 | 0.01485 | 0 | 0.0015 | 0 | 8.2192e-05 | 0 | 0.016432 | 6 | 0.5 | 1.201e-10 | 0.00033333 | 0.00033333
0.0011 | 910 | 2500 | 2.1713 | 1 | 3 | 4 | 3oo4 | 100 | 0.01 | 300 | 0.0033333 | 25% | 10000 | 0.0001 | 99% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.175 | 0.175 | 0.0010933 | 914.6412 | 2499.997 | 6 | 0.00013342 | 0.00086625 | 1.3613e-06 | 8.75e-05 | 3.0653e-09 | 4.7945e-06 | 0.0010933 | 24 | 0.6 | 4.8039e-10 | 0.0004 | 0.0004
Data for plotting:
Series labels: | MTBFdu = 50y |  | MTBFdu =100y
Voting | RRFAVG | MTTFS (years) | RRFAVG | MTTFS (years)
1oo1 | 95.4436 | 150 | 182.5685 | 150
1oo2 | 865.8511 | 75 | 1740.7257 | 75
1oo3 | 1902.7351 | 50 | 3648.5957 | 50
2oo2 | 47.7218 | 1498.358 | 91.2842 | 1498.358
2oo3 | 538.0825 | 997.813 | 1119.6378 | 997.813
2oo4 | 1574.3317 | 853.9343 | 3035.3566 | 853.9343
3oo3 | 31.8145 | 2999.9989 | 60.8562 | 2999.9989
3oo4 | 421.234 | 2499.997 | 914.6412 | 2499.997
STR ≈ [N! / (N-M)! . (λS + λDD)M . MTTR(M-1) ] + β . (λS + λDD)

## Variable parameters
© 2022 I&E Systems Pty Ltd
Round to | 2 | significant figures | [6 empty] | Shading indicates the cells for data entry | [22 empty] | The colour shading highlights the largest term
[8 empty] | (Years) | [9 empty] | (Years) |  | (days) | (years) | (days) | (years) | β for 1oo2 architecture |  | β for MooN architecture
PFDAVG | RRFAVG | MTTFS (years) |  |  | M | N | Voting | MTBFdu | λdu (pa) | MTBFdd | λdd | DC | MTBFdn | λdn | PTC | MTBFs | λS | T1 | T2 | MTTR | MTTR | MRT | MRT | β | βD | MooN β | MooN βD | PFDAVG | RRFAVG | MTTFS (years) |  | voted T1 term | CCF T1 term | voted T2 term | CCF T2 term | Voted λDD term | CCF λDD term | PFDAVG |  | STR β | Voted STR term | CCF STR term | STR
0.017 | 58 | 230 | Series 1 |  | 1 | 1 | 1oo1 | 30 | 0.033333 | 1000 | 0.001 | 2.913% | 10000 | 0.0001 | 99.7% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0 | 0 | 0.017125 | 58.3945 | 230.7692 | 1 | 0.016617 | 0 | 0.0005 | 0 | 8.2192e-06 | 0 | 0.017125 | 1 | 0 | 0.0043333 | 0 | 0.0043333
0.0055 | 180 | 230 |  |  | 1 | 1 | 1oo1 | 100 | 0.01 | 1000 | 0.001 | 9.091% | 10000 | 0.0001 | 99% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0 | 0 | 0.0054582 | 183.2099 | 230.7692 | 1 | 0.00495 | 0 | 0.0005 | 0 | 8.2192e-06 | 0 | 0.0054582 | 1 | 0 | 0.0043333 | 0 | 0.0043333
0.0021 | 470 | 230 |  |  | 1 | 1 | 1oo1 | 300 | 0.0033333 | 1000 | 0.001 | 23.08% | 10000 | 0.0001 | 97% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0 | 0 | 0.0021249 | 470.6135 | 230.7692 | 1 | 0.0016167 | 0 | 0.0005 | 0 | 8.2192e-06 | 0 | 0.0021249 | 1 | 0 | 0.0043333 | 0 | 0.0043333
0.00096 | 1000 | 230 |  |  | 1 | 1 | 1oo1 | 1000 | 0.001 | 1000 | 0.001 | 50% | 10000 | 0.0001 | 90% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0 | 0 | 0.00095822 | 1043.6026 | 230.7692 | 1 | 0.00045 | 0 | 0.0005 | 0 | 8.2192e-06 | 0 | 0.00095822 | 1 | 0 | 0.0043333 | 0 | 0.0043333
[26 empty] | 0 | 0 |  |  |  | #VALUE! | #VALUE! | 0 | #VALUE! | 0 | #VALUE! | 0 |  | 1 | 0 | #NUM! | 0
0.002 | 500 | 120 | Series 2 |  | 1 | 2 | 1oo2 | 30 | 0.033333 | 1000 | 0.001 | 2.913% | 10000 | 0.0001 | 99.7% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.1 | 0.1 | 0.002011 | 497.2746 | 115.3846 | 1 | 0.0002982 | 0.0016617 | 2.7e-07 | 5e-05 | 5.4719e-11 | 8.2192e-07 | 0.002011 | 2 | 0 | 0.0086667 | 0 | 0.0086667
0.00057 | 1700 | 120 |  |  | 1 | 2 | 1oo2 | 100 | 0.01 | 1000 | 0.001 | 9.091% | 10000 | 0.0001 | 99% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.1 | 0.1 | 0.00057255 | 1746.5581 | 115.3846 | 1 | 2.6463e-05 | 0.000495 | 2.7e-07 | 5e-05 | 5.4719e-11 | 8.2192e-07 | 0.00057255 | 2 | 0 | 0.0086667 | 0 | 0.0086667
0.00022 | 4600 | 120 |  |  | 1 | 2 | 1oo2 | 300 | 0.0033333 | 1000 | 0.001 | 23.08% | 10000 | 0.0001 | 97% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.1 | 0.1 | 0.00021558 | 4638.6204 | 115.3846 | 1 | 2.8227e-06 | 0.00016167 | 2.7e-07 | 5e-05 | 5.4719e-11 | 8.2192e-07 | 0.00021558 | 2 | 0 | 0.0086667 | 0 | 0.0086667
9.6e-05 | 10000 | 120 |  |  | 1 | 2 | 1oo2 | 1000 | 0.001 | 1000 | 0.001 | 50% | 10000 | 0.0001 | 90% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.1 | 0.1 | 9.6311e-05 | 10383.0653 | 115.3846 | 1 | 2.187e-07 | 4.5e-05 | 2.7e-07 | 5e-05 | 5.4719e-11 | 8.2192e-07 | 9.6311e-05 | 2 | 0 | 0.0086667 | 0 | 0.0086667
[26 empty] | #N/A | #N/A |  |  |  | #VALUE! | #VALUE! | #N/A | #VALUE! | #N/A | #VALUE! | #N/A |  | 1 | 0 | #NUM! | 0
0.0034 | 300 | 1500 | Series 3 |  | 2 | 3 | 2oo3 | 30 | 0.033333 | 1000 | 0.001 | 2.913% | 10000 | 0.0001 | 99.7% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.15 | 0.15 | 0.0033674 | 296.9629 | 1536.2729 | 3 | 0.00079797 | 0.0024925 | 7.225e-07 | 7.5e-05 | 1.4643e-10 | 1.2329e-06 | 0.0033674 | 6 | 1.5 | 9.2603e-07 | 0.00065 | 0.00065093
0.00089 | 1100 | 1500 |  |  | 2 | 3 | 2oo3 | 100 | 0.01 | 1000 | 0.001 | 9.091% | 10000 | 0.0001 | 99% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.15 | 0.15 | 0.00089027 | 1123.2576 | 1536.2729 | 3 | 7.0812e-05 | 0.0007425 | 7.225e-07 | 7.5e-05 | 1.4643e-10 | 1.2329e-06 | 0.00089027 | 6 | 1.5 | 9.2603e-07 | 0.00065 | 0.00065093
0.00033 | 3100 | 1500 |  |  | 2 | 3 | 2oo3 | 300 | 0.0033333 | 1000 | 0.001 | 23.08% | 10000 | 0.0001 | 97% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.15 | 0.15 | 0.00032701 | 3058.0211 | 1536.2729 | 3 | 7.5533e-06 | 0.0002425 | 7.225e-07 | 7.5e-05 | 1.4643e-10 | 1.2329e-06 | 0.00032701 | 6 | 1.5 | 9.2603e-07 | 0.00065 | 0.00065093
0.00015 | 6900 | 1500 |  |  | 2 | 3 | 2oo3 | 1000 | 0.001 | 1000 | 0.001 | 50% | 10000 | 0.0001 | 90% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0.15 | 0.15 | 0.00014504 | 6894.6142 | 1536.2729 | 3 | 5.8522e-07 | 6.75e-05 | 7.225e-07 | 7.5e-05 | 1.4643e-10 | 1.2329e-06 | 0.00014504 | 6 | 1.5 | 9.2603e-07 | 0.00065 | 0.00065093
[26 empty] | #N/A | #N/A |  |  |  | #VALUE! | #VALUE! | #N/A | #VALUE! | #N/A | #VALUE! | #N/A |  | 1 | 0 | #NUM! | 0
0.034 | 29 | 2300 | Series 4 |  | 2 | 2 | 2oo2 | 30 | 0.033333 | 1000 | 0.001 | 2.913% | 10000 | 0.0001 | 99.7% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0 | 0 | 0.03425 | 29.1973 | 2306.0496 | 2 | 0.033233 | 0 | 0.001 | 0 | 1.6438e-05 | 0 | 0.03425 | 2 | 1 | 3.0868e-07 | 0.00043333 | 0.00043364
0.011 | 92 | 2300 |  |  | 2 | 2 | 2oo2 | 100 | 0.01 | 1000 | 0.001 | 9.091% | 10000 | 0.0001 | 99% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0 | 0 | 0.010916 | 91.605 | 2306.0496 | 2 | 0.0099 | 0 | 0.001 | 0 | 1.6438e-05 | 0 | 0.010916 | 2 | 1 | 3.0868e-07 | 0.00043333 | 0.00043364
0.0042 | 240 | 2300 |  |  | 2 | 2 | 2oo2 | 300 | 0.0033333 | 1000 | 0.001 | 23.08% | 10000 | 0.0001 | 97% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0 | 0 | 0.0042498 | 235.3068 | 2306.0496 | 2 | 0.0032333 | 0 | 0.001 | 0 | 1.6438e-05 | 0 | 0.0042498 | 2 | 1 | 3.0868e-07 | 0.00043333 | 0.00043364
0.0019 | 520 | 2300 |  |  | 2 | 2 | 2oo2 | 1000 | 0.001 | 1000 | 0.001 | 50% | 10000 | 0.0001 | 90% | 300 | 0.0033333 | 1 | 10 | 3 | 0.0082192 | 3 | 0.0082192 | 0.1 | 0.1 | 0 | 0 | 0.0019164 | 521.8013 | 2306.0496 | 2 | 0.0009 | 0 | 0.001 | 0 | 1.6438e-05 | 0 | 0.0019164 | 2 | 1 | 3.0868e-07 | 0.00043333 | 0.00043364
Select variable for x-axis: |  |  | MTBFdu |  | Column: | 1
| RRFavg | [6 empty] | MTTFs
MTBFdu | 1oo1 | 1oo2 | 2oo3 | 2oo2 |  |  | MTBFdu | 1oo1 | 1oo2 | 2oo3 | 2oo2
30 | 58.3945 | 497.2746 | 296.9629 | 29.1973 |  |  | 30 | 230.7692 | 115.3846 | 1536.2729 | 2306.0496
100 | 183.2099 | 1746.5581 | 1123.2576 | 91.605 |  |  | 100 | 230.7692 | 115.3846 | 1536.2729 | 2306.0496
300 | 470.6135 | 4638.6204 | 3058.0211 | 235.3068 |  |  | 300 | 230.7692 | 115.3846 | 1536.2729 | 2306.0496
1000 | 1043.6026 | 10383.0653 | 6894.6142 | 521.8013 |  |  | 1000 | 230.7692 | 115.3846 | 1536.2729 | 2306.0496
| RRFavg plotted against varying MTBFdu | [6 empty] | MTTFs plotted against varying MTBFdu
STR = [N! / (N-M)! . (λS + λDD)M . MTTR(M-1) ] + β . (λS + λDD)

## MooN table
β multiplier | N |  |  |  |  | HFT corresponding to MooN architectures |  |  |  |  | Examples to illustrate STR β multiplier selection
M | 1 | 2 | 3 | 4 | 5 | 1 | 2 | 3 | 4 | 5 | PFD | STR |  | multiplier | row | col | STR N-M+1 | STR N
1 |  | 1 | 0.5 | 0.3 | 0.2 | 0 | 1 | 2 | 3 | 4 | 3oo3 | 1oo3 | tolerates 0 faults with 3 chances | 0 | 3 | 3 | 3 | 3
2 |  |  | 1.5 | 0.6 | 0.4 |  | 0 | 1 | 2 | 3 | 1oo3 | 3oo3 | tolerates 2 faults with 3 chances | 0.5 | 1 | 3 | 1 | 3
3 |  |  |  | 1.75 | 0.8 |  |  | 0 | 1 | 2 | 2oo3 | 2oo3 | tolerates 1 fault with 3 chances | 1.5 | 2 | 3 | 2 | 3
4 |  |  |  |  | 2 |  |  |  | 0 | 1 | 1oo4 | 4oo4 | tolerates 3 faults with 4 chances | 0.3 | 1 | 4 | 1 | 4
5 | [9 empty] | 0
[7 empty] | For PFD, MooN can tolerate N-M faults | [5 empty] | For STR, MooN can tolerate M-1 faults
The row selector is number of faults tolerated + 1, i.e. N-M+1,
the column selector is number of channels, N